## Notes
Bulk Asset Configurator
Author: | User A
Revision: | 3
Revision Date: | 2019-02-28
Template Notes: | Use this field to provide general notes about THIS particular Bulk Asset Configurator Template file.
READ THIS FIRST!
Sheets MUST be named: ClassInstantiation, ClassInstantiationRowsBased, ClassHistoryDefinitions, ClassAlarmDefinitions. The workbook must contain at least ClassInstantiation or ClassInstantiationRowsBased sheets (or both).
General Sheet Rules
Sheets without names recognized by the Bulk Asset Configurator, like this one, will be ignored.
Every sheet must contain a header row on the first row.
Bulk Asset Configurator reads all the lines in the sheet and skips lines that contain no values in mandatory columns.
Mandatory columns for ClassInstantiation are as follows: TargetEquipment, InstanceName, EquipmentClass and then your optional parameter columns.
Mandatory columns for ClassInstantiationRowsBased are as follows: TargetEquipment, InstanceName, EquipmentClass, ParameterName and ParameterValue. Every instance is repeated on as many rows, as there are parameters for this instance.
Mandatory columns for ClassHistoryDefinitions and ClassAlarmDefinitions are: EquipmentClass and Property. Historical and alarm columns are optional.
Please refer to the Historical Column Names and Alarm Column Names sheets for a list of recognized column names.
Column order is not important.
All paths can use either the forward slash (/) or the backslash (\) as a separator. The backslash is kept for compatibility reasons.
Special Parameters
/??acpath?/ This parameter forms a point name for the current Equipment. The Property is not included in the path. The result will be like 'ac:/Enterprise/Area/'.
/??path(separator, relativePath)?/ This parameter generates a generic path to the current Equipment. The Property is not included in the path. All arguments are optional. The separator argument can be a character or a short string that will get used to separate individual segments in the resulting path. The relativePath is concatenated with the path to the Equipment to form the final path. It is a forward slash separated path and can contain '..' segments to go up an level. For example, if the path to the Equipment is 'ac:/Enterprise/Area/', using the syntax /??path(.,../Area2)?/ will generate the result 'Enterprise.Area2'.
TargetHistoryFolder This parameter is added as a regular parameter on the ClassInstantiation or ClassInstantiationRowsBased sheets and specifies a target base folder in the historian where the history tags will get created. When this parameter is undefined, the target base folder will be chosen as normal to match the TargetEquipment + InstanceName. Please note, that changing the target base folder and running instantiation again will not delete the folders or tags created in the original folder - this is a limitation of the tool design.
TargetAlarmAreaXXX, where XXX is a positive number. These parameters are added as regular parameters on the ClassInstantiation or ClassInstantiationRowsBased sheets and specify the target base area for the alarm server where the alarm source links will get created. When none of these parameters are defined for a particular instance, the target base area will be chosen as normal to match the TargetEquipment + InstanceName. Please note that changing or omitting any target base area and running instantiation again will not delete the areas or source links created in the original area - this is a limitation of the tool design. Also note that alarms in non-standard areas will not get mapped properly to their corresponding Equipment or Property by the default rules provided for the alarm mapping rules engine, and that the rules engine can assign an alarm only to a single Equipment or Property.

## ClassInstantiation
TargetEquipment | InstanceName | EquipmentClass | DataInput_value | DESC | Display_Name | MeasurementPoint_002 | Unit_value | DigitalMeasurement | cmd_path | Dynamics_path | ExtraData_path | KKS_short | main_path | PID_path | pump_nb | Settings_path | SRU_CM_Pump | Status_path | ending | SPC_Wilenska_Zawor | Widocznosc_KR
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_E1_CisnZasil_SPCKartuska.value | 10 (AI01) Przetwornik cisnienia PT-E.1 |  | PT_E1_CisnZasil_SPCKartuska | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_E2_CisnPowr_SPCKartuska.value | 10 (AI01) Przetwornik cisnienia PT-E.2 |  | PT_E2_CisnPowr_SPCKartuska | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_E3_CisnZasil_SPCKartuska.value | 10 (AI01) Przetwornik cisnienia PT-E.3 |  | PT_E3_CisnZasil_SPCKartuska | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_E4_CisnPowr_SPCKartuska.value | 10 (AI01) Przetwornik cisnienia PT-E.4 |  | PT_E4_CisnPowr_SPCKartuska | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_Z1_CisnZasil_ZTPOK.value | 10 (AI01) Przetwornik cisnienia PT-Z.1 |  | PT_Z1_CisnZasil_ZTPOK | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_P1_CisnPowr_ZTPOK.value | 10 (AI01) Przetwornik cisnienia PT-P.1 |  | PT_P1_CisnPowr_ZTPOK | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_S1_CisnZasil_ZTPOK.value | 10 (AI01) Przetwornik cisnienia PT-S.1 |  | PT_S1_CisnZasil_ZTPOK | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_S2_CisnPowr_ZTPOK.value | 10 (AI01) Przetwornik cisnienia PT-S.2 |  | PT_S2_CisnPowr_ZTPOK | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_U1_CisnZasil_Ujescisko.value | 11 (AI02) Przetwornik cisnienia PT-U.1 |  | PT_U1_CisnZasil_Ujescisko | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_U2_CisnPowr_Ujescisko.value | 11 (AI02) Przetwornik cisnienia PT-U.2 |  | PT_U2_CisnPowr_Ujescisko | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_US1_Cisn_Przed_PSUx.value | 11 (AI02) Przetwornik cisnienia PT-US.1 |  | PT_US1_Cisn_Przed_PSUx | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PT_US2_Cisn_Za_PSUx.value | 11 (AI02) Przetwornik cisnienia PT-US.2 |  | PT_US2_Cisn_Za_PSUx | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PD_E1_CisnRozn_SPCKartuska.value | 11 (AI02) Przetwornik roznicy cisnien PD-E.1 |  | PD_E1_CisnRozn_SPCKartuska | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PD_S1_CisnRozn_ZTPOK.value | 11 (AI02) Przetwornik roznicy cisnien PD-S.1 |  | PD_S1_CisnRozn_ZTPOK | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.PD_U1_CisnRozn_Ujescisko.value | 11 (AI02) Przetwornik roznicy cisnien PD-U.1 |  | PD_U1_CisnRozn_Ujescisko | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_E1_TempZasil_SPCKartuska.value | 11 (AI02) Czujnik temperatury TT-E.1 |  | TT_E1_TempZasil_SPCKartuska | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_E2_TPowr_SPCKartuska.value | 12 (AI03) Czujnik temperatury TT-E.2 |  | TT_E2_TPowr_SPCKartuska | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_S1_TempZasil_ZTPOK.value | 12 (AI03) Czujnik temperatury TT-S.1 |  | TT_S1_TempZasil_ZTPOK | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_S2_TempPowr_ZTPOK.value | 12 (AI03) Czujnik temperatury TT-S.2 |  | TT_S2_TempPowr_ZTPOK | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_U1_TempZasil_Ujescisko.value | 12 (AI03) Przetwornik cisnienia TT-U.1 |  | TT_U1_TempZasil_Ujescisko | kPa
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_U2_TempPowr_Ujescisko.value | 12 (AI03) Czujnik temperatury TT-U.2 |  | TT_U2_TempPowr_Ujescisko | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_US1_TempPrzed_PSUx.value | 12 (AI03) Czujnik temperatury TT-US.1 |  | TT_US1_TempPrzed_PSUx | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_1_TempHalaPomp.value | 12 (AI03) Czujnik temperatury TT.1 |  | TT_1_TempHalaPomp | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_21_TempRozdzNN.value | 12 (AI03) Czujnik temperatury TT-2.1 |  | TT_21_TempRozdzNN | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_22_TempRozdzNN.value | 13 (AI04) Czujnik temperatury TT-2.2 |  | TT_22_TempRozdzNN | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_3_TempRozdzSN.value | 13 (AI04) Czujnik temperatury TT-3 |  | TT_3_TempRozdzSN | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_4_TempTrafo.value | 13 (AI04) Czujnik temperatury TT-4 |  | TT_4_TempTrafo | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_5_TempPomTechn.value | 13 (AI04) Czujnik temperatury TT-5 |  | TT_5_TempPomTechn | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_Z1_TempUzwPompy_POz1.value | 13 (AI04) Czujnik temperatury TT-Z.1 |  | TT_Z1_TempUzwPompy_POz1 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_Z2_TempUzwPompy_POz2.value | 13 (AI04) Czujnik temperatury TT-Z.2 |  | TT_Z2_TempUzwPompy_POz2 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_Z3_TempUzwPompy_POz3.value | 13 (AI04) Czujnik temperatury TT-Z.3 |  | TT_Z3_TempUzwPompy_POz3 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_P1_TempUzwPompy_POp1.value | 13 (AI04) Czujnik temperatury TT-P.1 |  | TT_P1_TempUzwPompy_POp1 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_P2_TempUzwPompy_POp2.value | 14 (AI05) Czujnik temperatury TT-P.2 |  | TT_P2_TempUzwPompy_POp2 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_P3_TempUzwPompy_POp3.value | 14 (AI05) Czujnik temperatury TT-P.3 |  | TT_P3_TempUzwPompy_POp3 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_Z4_TempPowietPompy_POz1.value | 14 (AI05) Czujnik temperatury TT-Z.4 |  | TT_Z4_TempPowietPompy_POz1 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_Z5_TempPowietPompy_POz2.value | 14 (AI05) Czujnik temperatury TT-Z.5 |  | TT_Z5_TempPowietPompy_POz2 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_Z6_TempPowietPompy_POz3.value | 14 (AI05) Czujnik temperatury TT-Z.6 |  | TT_Z6_TempPowietPompy_POz3 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_P4_TempPowietPompy_POp1.value | 14 (AI05) Czujnik temperatury TT-P.4 |  | TT_P4_TempPowietPompy_POp1 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_P5_TempPowietPompy_POp2.value | 14 (AI05) Czujnik temperatury TT-P.5 |  | TT_P5_TempPowietPompy_POp2 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_P6_TempPowietPompy_POp3.value | 14 (AI05) Czujnik temperatury TT-P.6 |  | TT_P6_TempPowietPompy_POp3 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.TT_6.value | 15 (AI06) Czujnik temperatury TT-6 |  | TT_6 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.MT_1_Temp_HalaPomp.value | 15 (AI06) Czujnik temperatury MT-1 |  | MT_1_Temp_HalaPomp | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.MT_1_Wilg_HalaPomp.value | 15 (AI06) Czujnik wilgotnosci MT-1 |  | MT_1_Wilg_HalaPomp
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz1_1_ZPTOK.value | 15 (AI06) Czujnik wibracji pompy POz-1.1 |  | Wib_POz1_1_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz1_2_ZPTOK.value | 15 (AI06) Czujnik wibracji pompy POz-1.2 |  | Wib_POz1_2_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz2_1_ZPTOK.value | 15 (AI06) Czujnik wibracji pompy POz-2.1 |  | Wib_POz2_1_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz2_2_ZPTOK.value | 15 (AI06) Czujnik wibracji pompy POz-2.2 |  | Wib_POz2_2_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz3_1_ZPTOK.value | 15 (AI06) Czujnik wibracji pompy POz-3.1 |  | Wib_POz3_1_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz3_2_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POz-3.2 |  | Wib_POz3_2_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp1_1_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POp-1.1 |  | Wib_POp1_1_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp1_2_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POp-1.2 |  | Wib_POp1_2_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp2_1_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POz-2.1 |  | Wib_POp2_1_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp2_2_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POp-2.2 |  | Wib_POp2_2_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp3_1_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POp-3.1 |  | Wib_POp3_1_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp3_2_ZPTOK.value | 16 (AI07) Czujnik wibracji pompy POp-3.2 |  | Wib_POp3_2_ZPTOK | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_VT_P41_POp1.value | 16 (AI07) Czujnik wibracji VT-P.4.1 |  | Wib_VT_P41_POp1 | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_VT_P42_POp2.value | 17 (AI08) Czujnik wibracji VT-P.4.2 |  | Wib_VT_P42_POp2 | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_VT_P43_POp3.value | 17 (AI08) Czujnik wibracji VT-P.4.3 |  | Wib_VT_P43_POp3 | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_VT_Z41_POz1.value | 17 (AI08) Czujnik wibracji VT-Z.4.1 |  | Wib_VT_Z41_POz1 | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_VT_Z42_POz2.value | 17 (AI08) Czujnik wibracji VT-Z.4.2 |  | Wib_VT_Z42_POz2 | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_VT_Z43_POz3.value | 17 (AI08) Czujnik wibracji VT-Z.4.3 |  | Wib_VT_Z43_POz3 | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp4_1_REZ.value | 17 (AI08) Czujnik wibracji pompy POp-4.1 REZERWA |  | Wib_POp4_1_REZ | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POp4_2_REZ.value | 17 (AI08) Czujnik wibracji pompy POp-4.2 REZERWA |  | Wib_POp4_2_REZ | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz4_1_REZ.value | 17 (AI08) Czujnik wibracji pompy POz-4.1 REZERWA |  | Wib_POz4_1_REZ | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Wib_POz4_2_REZ.value | 18 (AI09) Czujnik wibracji pompy POz-4.2 REZERWA |  | Wib_POz4_2_REZ | mms2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Temp_RA1.value | 18 (AI09) Czujnik temperatury w RA1 |  | Temp_RA1 | degC
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_1.value | 18 (AI09) Silownik ukladu wentylacji PK-1 |  | Sil_PK_1
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_2.value | 18 (AI09) Silownik ukladu wentylacji PK-2 |  | Sil_PK_2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_3.value | 18 (AI09) Silownik ukladu wentylacji PK-3 |  | Sil_PK_3
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_4.value | 18 (AI09) Silownik ukladu wentylacji PK-4 |  | Sil_PK_4
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_5.value | 18 (AI09) Silownik ukladu wentylacji PK-5 |  | Sil_PK_5
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_6.value | 18 (AI09) Silownik ukladu wentylacji PK-6 |  | Sil_PK_6
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_7.value | 19 (AI10) Silownik ukladu wentylacji PK-7 |  | Sil_PK_7
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PK_8.value | 19 (AI10) Silownik ukladu wentylacji PK-8 |  | Sil_PK_8
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PW_1.value | 19 (AI10) Silownik ukladu wentylacji PW-1 |  | Sil_PW_1
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PW_2.value | 19 (AI10) Silownik ukladu wentylacji PW-2 |  | Sil_PW_2
GPEC/Gdansk/Poludnie/Super_SPC | /?MeasurementPoint_002?/ | GPEC/Pomiary//?MeasurementPoint_002?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC/Unit_Measurements/EM_InputConditioning.Sil_PW_3.value | 19 (AI10) Silownik ukladu wentylacji PW-3 |  | Sil_PW_3
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSA_E1_Zasil_SPCKartuska | 05 (DI2) Rozdzielnica wywietrzaka WZ3 sygnalizacja 2 biegu pracy |  |  |  | PSA_E1_Zasil_SPCKartuska
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSA_E2_Powr_SPCKartuska | 05 (DI2) Rozdzielnica wywietrzaka WZ3 sygnalizacja awarii |  |  |  | PSA_E2_Powr_SPCKartuska
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSA_S1_Zasil_ZTPOK | 05 (DI2) Styk pomocniczy aparatu SPD w RGNN sygnalizacja awarii |  |  |  | PSA_S1_Zasil_ZTPOK
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSA_S2_Powr_ZTPOK | 05 (DI2) Zasilacz 12.3Z1 styk prawidłowej pracy |  |  |  | PSA_S2_Powr_ZTPOK
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSA_US1_Przed_PSU | 05 (DI2) Zasilacz 12.3Z2 styk prawidłowej pracy |  |  |  | PSA_US1_Przed_PSU
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSA_US2_Za_PSU | 05 (DI2) Modul redundancji zasilania DC rownowaga zasilaczy |  |  |  | PSA_US2_Za_PSU
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.LCA11 | 05 (DI2) Modul redundancji zasilania DC redundancja sprawna |  |  |  | LCA11
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.LC12 | 05 (DI2) Zabezpieczenie obwodow DC 12.4Z2 praca prawidlowa |  |  |  | LC12
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.LC13 | 05 (DI2) Rozdzielnica SN wyl. w polu 9 wylacznik zamkniety |  |  |  | LC13
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.SSP_Usterka | 05 (DI2) Rozdzielnica SN wyl. w polu 9 wylacznik otwarty |  |  |  | SSP_Usterka
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.SSWIN | 05 (DI2) Rozdzielnica SN wyl. w polu 6 wylacznik zamkniety |  |  |  | SSWIN
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ1_1bieg | 05 (DI2) Rozdzielnica SN wyl. w polu 6 wylacznik otwarty |  |  |  | WZ1_1bieg
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ1_2bieg | 05 (DI2) Centrala SSP alarm pozaru 1 stopnia |  |  |  | WZ1_2bieg
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ1_Aw | 05 (DI2) Centrala SSP alarm pozaru 2 stopnia |  |  |  | WZ1_Aw
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ2_1bieg | 06 (DI3) Rozdzielnica SN sygnal obecnosci napiecia zasilania |  |  |  | WZ2_1bieg
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ2_2bieg | 06 (DI3) Presostat wysokiego cis. PSAH-E.3 |  |  |  | WZ2_2bieg
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ2_Aw | 06 (DI3) Presostat wysokiego cis. PSAH-E.4 |  |  |  | WZ2_Aw
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ3_1bieg | 06 (DI3) Zabezpieczenie obwodow DC 12.4Z3 praca prawidlowa |  |  |  | WZ3_1bieg
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ3_2bieg | 06 (DI3) Sygnalizacja zbiorcza zabezpieczen napedow armatury w RGNN |  |  |  | WZ3_2bieg
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.WZ3_Aw | 06 (DI3) Sygnalizacja zbiorcza zabezpieczen oswietlenia w RGNN |  |  |  | WZ3_Aw
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.RGNN_Aw | 06 (DI3) Sygnalizacja zbiorcza zabezpieczen PZ-1, PZ-2 klimatyzacji i wywietrznikow |  |  |  | RGNN_Aw
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.Zasilacz123Z1_OK | 06 (DI3) Sygnalizacja zbiorcza zabezpieczen napedow w RGN |  |  |  | Zasilacz123Z1_OK
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.SSP_P1 |  |  |  |  | SSP_P1
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.SSP_P2 |  |  |  |  | SSP_P2
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.SN_Zas_OK |  |  |  |  | SN_Zas_OK
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSAH_E3_Zasil_SPCKartuska |  |  |  |  | PSAH_E3_Zasil_SPCKartuska
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.PSAH_E4_Powr_SPCKartuska |  |  |  |  | PSAH_E4_Powr_SPCKartuska
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.Zab_124Z3_OK |  |  |  |  | Zab_124Z3_OK
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.Zab_Nap_RGNN |  |  |  |  | Zab_Nap_RGNN
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.Zab_Osw_RGNN |  |  |  |  | Zab_Osw_RGNN
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.Zab_PZ_1_PZ_2_kl_wyw |  |  |  |  | Zab_PZ_1_PZ_2_kl_wyw
GPEC/Gdansk/Poludnie/Super_SPC | /?DigitalMeasurement?/ | GPEC//?DigitalMeasurement?/ | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC.Zab_Nap_RGN |  |  |  |  | Zab_Nap_RGN
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 1
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 2
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 3
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 4
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 5
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 6
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 7
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 8
GPEC/Gdansk/Poludnie/Super_SPC | /?SRU_CM_Pump?/ | GPEC/Napedy//?SRU_CM_Pump?/ | [10 empty] | ua:SCADA-APP\\[KEPServerEX]Super_SPC/Super_SPC |  | 9
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_1 | ZP1
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_2 | ZP3
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_3 | ZP4
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_4 | ZP5
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_5 | ZK23
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_6 | ZP9
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_7 | ZP11
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_8 | ZK24
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_9 | ZP10
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_10 | ZP1
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_11 | ZP2
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_12 | ZP6
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_13 | ZP7
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_14 | ZP8
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_15 | ZK25
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_16 | ZP13
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_17 | ZP16
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_18 | ZK26
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_19 | ZP14
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_20 | ZP15
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_21 | ZP17
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_22 | ZP18
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_23 | ZK1
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_24 | ZK2
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_25 | ZP19
GPEC/Gdansk/Poludnie/Super_SPC | /?SPC_Wilenska_Zawor?/ | GPEC/Zawory//?SPC_Wilenska_Zawor?/ | [16 empty] | ending_26 | ZP20

## ClassInstantiationRowsBased
TargetEquipment | InstanceName | EquipmentClass | ParameterName | ParameterValue

## ClassHistoryDefinitions
EquipmentClass | Property | GenerateHistory | HistoryTagType | Enabled | IsCollected | LoggingGroup | CollectorGroup | DataType | SteppedInterpretation | SupportOperatorComments | SupportOPCDABackfilling | EngineeringUnits | LowRange | HighRange | SourceType | DatasetName | LogGoodSamplesOnly | FilterType | DeadbandType | DeadbandValue | FilterThresholdInterpretation | FilterThreshold | FilterMinPeriod | FilterMaxPeriod | AggregateType | UseUniversalTime | StartTime | PercentGood | TreatUncertainAsBad | UseShutdownMarker | UseCollectionPeriod | CollectionPeriod | UseAlternateCalculationPeriod | AlternateCalculationPeriod | MovAvgWeight | TotalizerUnits | MROT_UseUniversalTime | MROT_RecurrenceType | MROT_Start | MROT_SimplePeriod | MROT_PeriodMultiplier | MROT_Period | MROT_ActiveDaySpecification | MROT_Months | MROT_DaysOfMonth | MROT_WeeksOfMonth | MROT_DaysOfWeek | MROT_UseAdvancedTime | MROT_Hours | MROT_Minutes | MROT_Seconds | Expression | MinTimeBetweenSamples | ConditionClass | TriggerName1 | TriggerPath1 | TriggerSpcType1 | AggregateName1 | AggregateDisplayName1 | AggregateEnabled1 | AggregateType1 | AggregateGroup1 | DataSource | RuleSet | ReportViolatedRules | CollectionType | SubgroupSize | NSigma | SquelchPeriod | Pri_HighRange | Pri_LowRange | Sec_HighRange | Sec_LowRange | Limits_Type | Limits_RecalcRate | Limits_RecalcHistorySize | Mu | Sigma | Pri_UCL | Pri_CL | Pri_LCL | Sec_UCL | Sec_CL | Sec_LCL | Spec_LimitType | Spec_UCL | Spec_CL | Spec_LCL | Stats_Type | Stats_RecalcRate | Stats_RecalcHistorySize | DataIsNormal | Stats_CapabilityRatios
Heating control | CurrentTemperature | TRUE | N | TRUE | TRUE | Sample Logging Group | Collector Group (1 second) | Float64 | FALSE | TRUE | FALSE | °C | -20 | 50 | Datapoint |  | FALSE | NoFilter | Percent | 0 | Percent | 1 | 0:00:00.5 | 0:01:00.0 | AllSamples | FALSE | 36526 | 90 | TRUE | TRUE | FALSE | 0:00:05.0 | FALSE | 0:00:10.0 | 0.5 | Second | FALSE | Simple | 36526 | 0:00:05.0 | 1 | Years | DayOfWeek | Jan |  | first, second | weekday | TRUE | 12 | 30 | 0 | [6 empty] | Count_1min | Count (1min) | TRUE | Count | Sample Logging Group/Aggregate Group (1 minute)
Heating control | HeatingLevel | TRUE | N | TRUE | TRUE | Sample Logging Group | Collector Group (1 second) | Float64 | FALSE | TRUE | FALSE | W | 0 | 1000 | Datapoint |  | FALSE | NoFilter | Percent | 0 | Percent | 1 | 0:00:00.5 | 0:01:00.0 | AllSamples | FALSE | 36526 | 90 | TRUE | TRUE | FALSE | 0:00:05.0 | FALSE | 0:00:10.0 | 0.5 | Second | FALSE | Simple | 36526 | 0:00:05.0 | 1 | Years | DayOfWeek | Feb |  | first, second | weekday | TRUE | 12 | 30 | 0
Heating control | Consumption | TRUE | C | TRUE |  | Sample Logging Group |  | Float64 | FALSE | FALSE |  | KWh | 0 | 1000 | [37 empty] | calcprev() + (val(tagtotalize({{data:/??path(.,HeatingLevel)?/}}, utcnow() - fromminutes(1), fromminutes(1), 0)) / 3600000) | 0:00:00.0 |  | 1min | Periodic/1min
Heating control | TemperatureLimit | TRUE | CC | TRUE |  | Sample Logging Group | [45 empty] | IF {{data:/??path(.,CurrentTemperature)?/}} <= 12 THEN -1 ELSE 0 |  | LimitAlarm | 1s | Periodic/1s

## ClassAlarmDefinitions
EquipmentClass | Property | GenerateAlarm | AlarmTemplate | Enabled | DefaultDisplay | Delay | BaseText | HelpText | EnableClear | ExcludeEqualTo | OffDelay | LatchAck | LatchUnack | OutOfService | Suppress | ReAlarm | ReAlarmTime | Shelve | ShelveTime | IgnoreBadQuality | Weight | AlarmSourceType | Input2 | Deadband | AckOnRTN | RTNText | LoLoLimit | LoLoMsgText | LoLoSeverity | LoLoRequiresAck | LoLimit | LoMsgText | LoSeverity | LoRequiresAck | HiLimit | HiMsgText | HiSeverity | HiRequiresAck | HiHiLimit | HiHiMsgText | HiHiSeverity | HiHiRequiresAck | Limit | MsgText | Severity | RequiresAck | TlaRequiresAck | TlaHeartBeat | RelatedValue1 | RelatedValue2 | RelatedValue3 | RelatedValue4 | RelatedValue5 | RelatedValue6 | RelatedValue7 | RelatedValue8 | RelatedValue9 | RelatedValue10 | RelatedValue11 | RelatedValue12 | RelatedValue13 | RelatedValue14 | RelatedValue15 | RelatedValue16 | RelatedValue17 | RelatedValue18 | RelatedValue19 | RelatedValue20 | AlarmSourceName
Heating control | CurrentTemperature | TRUE |  | 1 | [7 empty] | FALSE | FALSE | 1 | 1 | FALSE |  | 1 |  |  |  | L |  | 0 | 0 | Temperature normal | 0 | Freezing | 900 | 1 | 4 | Cold | 800 | 1 | 80 | Hot | 800 | 1 | 100 | Boiling | 900 | 1
Heating control | HeatingLevel | TRUE |  | 1 | [7 empty] | FALSE | FALSE | 1 | 1 | FALSE |  | 1 |  |  |  | D |  |  | 0 | Heating on | [16 empty] | 0 | Heating off | 100 | 0

## Historical Column Names
Column name | Data type | HistoryTagType | Description | Enumerations
AggregateDisplayNameXXX | String | N | Add one or mutliple columns of this type and replace XXX with a number. Each set will add a new Aggregate to a historical tag
AggregateEnabledXXX | Boolean | N | Add one or mutliple columns of this type and replace XXX with a number. Each set will add a new Aggregate to a historical tag
AggregateGroupXXX | reference | N | Add one or mutliple columns of this type and replace XXX with a number. Each set will add a new Aggregate to a historical tag
AggregateNameXXX | String | N | Add one or mutliple columns of this type and replace XXX with a number. Each set will add a new Aggregate to a historical tag
AggregateType | enumeration | N | Defines the aggregate used to filter data on collector. | AllSamples | Max | Min | Avg | StdDev | RunningMax | RunningMin | RunningAvg | MovingAvg | MovingMax | MovingMin | Totalizer | MostRecentOnTime
AggregateTypeXXX | enumeration | N | Add one or mutliple columns of this type and replace XXX with a number. Each set will add a new Aggregate to a historical tag | None | Interpolative | Average | TimeAverage | Sum | Total | Minimum | Maximum | MinimumActualTime | MaximumActualTime | Range | AnnotationCount | Count | DurationInState0 | DurationInState1 | NumberOfTransitions | Start | End | Delta | DurationGood | DurationBad | PercentGood | PercentBad | WorstQuality | StdDev | Variance | StdDev2 | Variance2 | StartBound | EndBound | DeltaBound | Minimum2 | Maximum2 | MinimumActualTime2 | MaximumActualTime2 | Range2 | TimeAverage2 | Total2 | WorstQuality2
AlternateCalculationPeriod | TimeSpan | N | Alternate calculation period value. Units in DB are milliseconds. Must be enabled by UseAlternateCalculationPeriod
CollectionPeriod | TimeSpan | N | Collection period value. Units in DB are milliseconds. Must be enabled by UseCollectionPeriod
CollectionType | enumeration | SPC | The SPC collection type | None | XBarR | XBarS | MedianR | XMR
CollectorGroup | reference | N | Defines to which Collector Group this tag belongs. Must be set if tag is Collected
ConditionClass | reference | CSE, CC | Database reference to the Condition Class. Only applies if this tag generates events of some sort.
DataIsNormal | Boolean | SPC | Specifies if data is normal
DatasetName | String | N | DatasetName - standardized or generic. Can be empty.
DataSource | String | SPC | Source of data to be logged (Data point)
DataType | enumeration | N, C | The data type of the logged value. | Native | Float64 | Float32 | Int8 | Int16 | Int32 | Int64 | UInt8 | UInt16 | UInt32 | UInt64 | String | Boolean | Duration | DateTime | Float64Array | Float32Array | Int8Array | Int16Array | Int32Array | Int64Array | UInt8Array | UInt16Array | UInt32Array | UInt64Array | StringArray | BooleanArray | DurationArray | DateTimeArray
DeadbandType | enumeration | N | Defines meaning of Threshold value, either percent or absolute. Deadband only. | Percent | Absolute
DeadbandValue | Double | N | Value defining filter threshold. Deadband only.
Enabled | Boolean | N, C, CSE, CC | if true, tag is Enabled. Otherwise NOT loaded by runtime.
EngineeringUnits | String | N, C, SPC | Name of the engineering units that will be used for the current signal.
Expression | String | C, CSE, CC | Expression, represents what the function will do
FilterMaxPeriod | TimeSpan | N | Maximum time to elapse between two consecutive writes (from filter). Swinging Door only. Units in DB are milliseconds.
FilterMinPeriod | TimeSpan | N | Minimum time to elapse between two consecutive writes (from filter). Swinging Door only. Units in DB are milliseconds.
FilterThreshold | Double | N | Value defining filter threshold (absolute or percentage) Swinging Door only.
FilterThresholdInterpretation | enumeration | N | Defines meaning of Threshold value, either percent or absolute. Swinging Door only. | Percent | Absolute
FilterType | enumeration | N | FilterType, such as Deadband / Swinging door | NoFilter | Deadband | SwingingDoor
GenerateHistory | Boolean | N, C, CSE, CC, SPC
HighRange | Double | N, C | Tag's High Limit
HistoryTagType | enumeration |  | Chooses between Normal (N), Calculated (C), Calculated Simple Events (CSN), Calculated Condition (CC) and SPC tag type (SPC). Defaults to N. | N | C | CSE | CC | SPC
IsCollected | Boolean | N | If true, tag is collected by collector. DataSource must be defined.
Limits_RecalcHistorySize | String | SPC | The number of last N subgroups
Limits_RecalcRate | String | SPC | Calculation rate if calculated limits
Limits_Type | enumeration | SPC | Specifies the calculated limits type. | CalculatedAll | CalculatedLastN | CalculatedMuSigma | Constant
LoggingGroup | reference | N, C, CSE, CC, SPC | Defines to which Logging Group this tag belongs. Must be set if tag is NOT Collected.
LogGoodSamplesOnly | Boolean | N | Log good smples only.
LowRange | Double | N, C | Tag's Low Limit
MinTimeBetweenSamples | TimeSpan | C | Defines the time distance, in seconds and milliseconds, between calculated samples. Unit in DB is seconds.
MovAvgWeight | Single | N | Weight for exponentially weighted moving aggregate calculation, valid range is between 0 and 1. For Moving Average Collector Aggregate only.
MROT_ActiveDaySpecification | enumeration | N | Specifies whether the 'Day of Month' or 'Day of Week' patterns are used. Only meaningful when MROT_Period is set to <see cref="F:Ico.Fwx.Triggers.TimeTriggers.RecurrencePeriod.Months" /> or <see cref="F:Ico.Fwx.Triggers.TimeTriggers.RecurrencePeriod.Years" /> | DayOfMonth | DayOfWeek
MROT_DaysOfMonth | Int64 | N | A list of days in the month. Like the 1st, 2nd, 28th, last.
MROT_DaysOfWeek | Int64 | N | Days of week, like monday, tuesday, weekday, weekend day.
MROT_Hours | Int64 | N | List of hours, from 0 to 23.
MROT_Minutes | Int64 | N | List of minutes from 0 to 59.
MROT_Months | Int64 | N | Months, like january, december.
MROT_Period | enumeration | N | The recurrence period. Used with a <see cref="F:Ico.Fwx.Triggers.TimeTriggers.RecurrenceType.Complex" />MROT_RecurrenceType. | Seconds | Minutes | Hours | Days | Weeks | Months | Years
MROT_PeriodMultiplier | Int32 | N | The MROT_Period is multiplied by this number. For example for the period of two hours means that only every second hour (relative to the 'MROT_Start' time) will be effective and it's minute and seconds schedules will be executed. Must be greater than 0.
MROT_RecurrenceType | enumeration | N | The type of recurence. | Once | Simple | Complex
MROT_Seconds | Int64 | N | List of seconds from 0 to 59.
MROT_SimplePeriod | TimeSpan | N | Simple Period used together with a 'MROT_RecurrenceType' of type 'Simple'.
MROT_Start | DateTime | N | The 'Starting at' setting.
MROT_UseAdvancedTime | Boolean | N | If set, MROT_Hours, MROT_Minutes and MROT_Seconds will be used. If not set, the hours, minutes and seconds specified by MROT_Start will be used.
MROT_UseUniversalTime | Boolean | N | Whether to use UTC or not.
MROT_WeeksOfMonth | Int64 | N | To specify which day of week in the month is meant, if it is the first, second, last...
Mu | String | SPC | The constant Mean value for calculated limits
NSigma | Double | SPC | NSigma value
PercentGood | Single | N | Defines how long (in percent of calculation interval) have to have value Good quality status to create Good quality calculated value. For Collector Aggregate filtering except Std. Dev and Most Recent On Time.
Pri_CL | String | SPC | The primary chart CL value. To be specified if the LimitsType is DefaultTarget.
Pri_HighRange | Double | SPC | Specifies the high limit of primary chart.
Pri_LCL | String | SPC | The primary chart LCL value. To be specified if the LimitsType is DefaultTarget.
Pri_LowRange | Double | SPC | Specifies the low limit for primary chart.
Pri_UCL | String | SPC | The primary chart UCL value. To be specified if the LimitsType is DefaultTarget.
ReportViolatedRules | Boolean | SPC | Specifies if we want to report violated rules
RuleSet | reference | SPC | Associated SPC distribution rule
Sec_CL | String | SPC | The primary chart CL value. To be specified if the LimitsType is DefaultTarget.
Sec_HighRange | Double | SPC | Specifies the high range of secondary chart.
Sec_LCL | String | SPC | The secondary chart LCL value. To be specified if the LimitsType is DefaultTarget.
Sec_LowRange | Double | SPC | Specifies the low limit of the secondary chart.
Sec_UCL | String | SPC | The secondary chart UCL value. To be specified if the LimitsType is DefaultTarget.
Sigma | String | SPC | The Sigma constant value of calculated limits.
SourceType | enumeration | N | SourceType of a input signal (Data-point, Dataset, Dataset Generic) | Datapoint | Dataset | DatasetGeneric
Spec_CL | String | SPC | Specifies the target.
Spec_LCL | String | SPC | Specifies the lower specification level.
Spec_LimitType | enumeration | SPC | Specifies the type of the limits for statistics. | All | Upper | Lower | DefaultTarget
Spec_UCL | String | SPC | Specifies the upper specification limit.
SquelchPeriod | Int32 | SPC | Squelch Period.
StartTime | DateTime | N | Calculation period startTime for Collector Aggregate filtering except Most Recent On Time.
Stats_CapabilityRatios | enumeration | SPC | The process capability ratios. (Cp, Cpu, Cpl, Cpk, Cpm, Cpkm, Cr, Pp, Ppu, Ppl, Ppk, Ppm, Ppkm, Pr, Mean, Sigma, Avg, StdDev, Skew, Kurtosis) | None | Cp | Cpu | Cpl | Cpk | Cpm | Cpkm | Cr | Pp | Ppu | Ppl | Ppk | Ppm | Ppkm | Pr | Mean | Sigma | Avg | StdDev | Skew | Kurtosis
Stats_RecalcHistorySize | String | SPC | The number of last N subgroups for statistics calculation
Stats_RecalcRate | String | SPC | Calculation rate for statistics calculation.
Stats_Type | enumeration | SPC | Specifies the statistics calculation type. | CalculatedAll | CalculatedLastN
SteppedInterpretation | Boolean | N, C | If true, the nearest older available value will be used as tag value reading at a given time-stamp. Otherwise, the value will be interpreted from neighboring values. Only for numeric data types.
SubgroupSize | Byte | SPC | The size of the subgroup or sub range
SupportOPCDABackfilling | Boolean | N | Enables backfilling from devices via OPC DA. Disables all filters on collector.
SupportOperatorComments | Boolean | N, C | If true, Operator Comments (Annotations) are allowed for this tag.
TotalizerUnits | enumeration | N | Totalizer Units for Collector Totalizer filtering | Second | Minute | Hour | Day
TreatUncertainAsBad | Boolean | N | If true, samples with uncertain quality are treated as bad. For Collector Aggregate filtering except Most Recent On Time.
TriggerNameXXX | String | C, CSE, CC, SPC | Add one or mutliple columns of this type and replace XXX with a number. Each pair of TriggerNameXXX and TriggerPathXXX will add a new trigger reference. For SPC tags, also add a TriggerSpcTypeXXX column.
TriggerPathXXX | reference | C, CSE, CC, SPC | See TriggerNameXXX. Put a reference to an already preconfigured trigger into this column, for example Periodic/1min
TriggerSpcTypeXXX | enumeration | SPC | See TriggerNameXXX. Put a SPC trigger type into this column. | None | ResetLimits | StartBatch
UseAlternateCalculationPeriod | Boolean | N | True when alternate calculation period should be used. For Collector Aggregate filtering only (Does not apply to Moving, Totalizer and Most Recent On Time).
UseCollectionPeriod | Boolean | N | True when collection period should be used instead of sampling period specified on collector. For Collector Aggregate (Running and Moving) filtering only.
UseShutdownMarker | Boolean | N | If true, BadNoData sample is stored next to last aggregated sample. For Collector Aggregate filtering only.
UseUniversalTime | Boolean | N | Specifies if the tag is using universal time or not

## Alarm Column Names
Column name | Alternative name | Data type | AlarmSourceType | Description | Enumerations
AlarmSourceName |  | String | L, D, DEV, ROC, RLM, TLA | A user defined name for the generated alarm source. It is recommended to leave empty and the tool will fill in one automatically. As each alarm definition line creates multiple alarm sources, it is up to the user to make sure that any value specified here is sufficiently parametrized to generate unique alarm sources.
AlarmSourceType | LimitOrDigital(L/D) | enumeration |  |  | L | D | DEV | ROC | RLM | TLA
AlarmTemplate |  | reference | L, D, DEV, ROC, RLM, TLA | Template ID.
BaseText |  | String | L, D, DEV, ROC, RLM, TLA | Base Text
DefaultDisplay |  | String | L, D, DEV, ROC, RLM, TLA | Default Display.
Delay |  | String | L, D, DEV, ROC, RLM, TLA | Delay (seconds).
DevAckOnRTN | AckOnRTN | String | DEV
DevDeadband | Deadband | String | DEV | Deadband.
DevHiHiLimit | HiHiLimit | String | DEV
DevHiHiMsgText | HiHiMsgText | String | DEV
DevHiHiRequiresAck | HiHiRequiresAck | String | DEV
DevHiHiSeverity | HiHiSeverity | String | DEV
DevHiLimit | HiLimit | String | DEV
DevHiMsgText | HiMsgText | String | DEV
DevHiRequiresAck | HiRequiresAck | String | DEV
DevHiSeverity | HiSeverity | String | DEV
DevInput2 | Input2 | String | DEV | OPC Input 2.
DevLoLimit | LoLimit | String | DEV
DevLoLoLimit | LoLoLimit | String | DEV
DevLoLoMsgText | LoLoMsgText | String | DEV
DevLoLoRequiresAck | LoLoRequiresAck | String | DEV
DevLoLoSeverity | LoLoSeverity | String | DEV
DevLoMsgText | LoMsgText | String | DEV
DevLoRequiresAck | LoRequiresAck | String | DEV
DevLoSeverity | LoSeverity | String | DEV
DevRTNText | RTNText | String | DEV
DigAckOnRTN | AckOnRTN | String | D
DigAlarmState | Limit | String | D
DigInput2 | Input2 | String | D | OPC Override Input
DigMsgText | MsgText | String | D
DigRequiresAck | RequiresAck | String | D
DigRTNText | RTNText | String | D
DigSeverity | Severity | String | D
EnableClear |  | String | L, D, DEV, ROC, RLM, TLA | Enable Clear. Put "1" for true and leave empty for false.s
Enabled |  | String | L, D, DEV, ROC, RLM, TLA | Enabled.
ExcludeEqualTo |  | String | L, D, DEV, ROC, RLM, TLA | Exclude Equal To. Put "1" for true and leave empty for false.
GenerateAlarm |  | Boolean | L, D, DEV, ROC, RLM, TLA
HelpText |  | String | L, D, DEV, ROC, RLM, TLA | Help Instructions.
IgnoreBadQuality |  | Boolean | L, D, DEV, ROC, RLM, TLA | Ignore Bad Quality
LatchAck |  | Boolean | L, D, DEV, ROC, RLM, TLA | Latch Ack
LatchUnack |  | Boolean | L, D, DEV, ROC, RLM, TLA | Latch UnAck
LimAckOnRTN | AckOnRTN | String | L
LimDeadband | Deadband | String | L | Deadband.
LimHiHiLimit | HiHiLimit | String | L
LimHiHiMsgText | HiHiMsgText | String | L
LimHiHiRequiresAck | HiHiRequiresAck | String | L
LimHiHiSeverity | HiHiSeverity | String | L
LimHiLimit | HiLimit | String | L
LimHiMsgText | HiMsgText | String | L
LimHiRequiresAck | HiRequiresAck | String | L
LimHiSeverity | HiSeverity | String | L
LimInput2 | Input2 | String | L | OPC Override Input.
LimLoLimit | LoLimit | String | L
LimLoLoLimit | LoLoLimit | String | L
LimLoLoMsgText | LoLoMsgText | String | L
LimLoLoRequiresAck | LoLoRequiresAck | String | L
LimLoLoSeverity | LoLoSeverity | String | L
LimLoMsgText | LoMsgText | String | L
LimLoRequiresAck | LoRequiresAck | String | L
LimLoSeverity | LoSeverity | String | L
LimRTNText | RTNText | String | L
OffDelay |  | String | L, D, DEV, ROC, RLM, TLA | Off Delay
OutOfService |  | String | L, D, DEV, ROC, RLM, TLA | Out of Service
ReAlarm |  | Boolean | L, D, DEV, ROC, RLM, TLA | ReAlarm
ReAlarmTime |  | String | L, D, DEV, ROC, RLM, TLA | ReAlarmTime
RelatedValue1 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue2 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue3 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue4 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue5 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue6 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue7 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue8 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue9 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue10 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue11 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue12 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue13 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue14 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue15 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue16 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue17 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue18 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue19 |  | String | L, D, DEV, ROC, RLM, TLA
RelatedValue20 |  | String | L, D, DEV, ROC, RLM, TLA
RlmAckOnRTN | AckOnRTN | String | RLM
RlmDeadband | Deadband | String | RLM | Deadband.
RlmHiHiLimit | HiHiLimit | String | RLM
RlmHiHiMsgText | HiHiMsgText | String | RLM
RlmHiHiRequiresAck | HiHiRequiresAck | String | RLM
RlmHiHiSeverity | HiHiSeverity | String | RLM
RlmHiLimit | HiLimit | String | RLM
RlmHiMsgText | HiMsgText | String | RLM
RlmHiRequiresAck | HiRequiresAck | String | RLM
RlmHiSeverity | HiSeverity | String | RLM
RlmInput2 | Input2 | String | RLM | OPC Override Input.
RlmLoLimit | LoLimit | String | RLM
RlmLoLoLimit | LoLoLimit | String | RLM
RlmLoLoMsgText | LoLoMsgText | String | RLM
RlmLoLoRequiresAck | LoLoRequiresAck | String | RLM
RlmLoLoSeverity | LoLoSeverity | String | RLM
RlmLoMsgText | LoMsgText | String | RLM
RlmLoRequiresAck | LoRequiresAck | String | RLM
RlmLoSeverity | LoSeverity | String | RLM
RlmRTNText | RTNText | String | RLM
RocAckOnRTN | AckOnRTN | String | ROC
RocInput2 | Input2 | String | ROC | OPC Override Input.
RocLimit | Limit | String | ROC
RocMsgText | MsgText | String | ROC
RocRequiresAck | RequiresAck | String | ROC
RocRTNText | RTNText | String | ROC
RocSeverity | Severity | String | ROC
Shelve |  | String | L, D, DEV, ROC, RLM, TLA | Shelve
ShelveTime |  | String | L, D, DEV, ROC, RLM, TLA | Shelve Time
Suppress |  | String | L, D, DEV, ROC, RLM, TLA | Suppress
TlaEnable | Limit | String | TLA
TlaHeartBeat |  | Int32 | TLA
TlaInput2 | Input2 | String | TLA | OPC Override Input.
TlaMsgText | MsgText | String | TLA
TlaRequiresAck | RequiresAck | String | TLA
TlaSeverity | Severity | String | TLA
Weight |  | Boolean | L, D, DEV, ROC, RLM, TLA | Weight